{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":47,"n_cols":8,"rows_kept":47,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","AZAS-MY1"]
[]
[]
[]
[]
["","","","","","AZAS100M7Y1B","AZAS125M7Y1B","AZAS140M7Y1B"]
["Dimensiuni","Unitate","","Înălțime","mm","990","990","990"]
["","","","Lățime","mm","940","940","940"]
["","","","Adâncime","mm","320","320","320"]
["Greutate","Unitate","","","kg","","70"]
["Compresor","Type","","","","","Compresor swing etanşat ermetic"]
["Gama de operare","Răcire","Ambiant","Min.","°CDB","-5","-5","-5"]
["","","","Max.","°CDB","46","46","46"]
["","Încălzire","Ambiant","Min.","°C termometru umed","-15","-15","-15"]
["","","","Max.","°C termometru umed","15.5","15.5","15.5"]
["Nivel de putere sonoră","Răcire","","","dBA","70","71","73"]
["","Încălzire","","","dBA","","71","73 (1)"]
["Nivelul de presiune sonoră","Răcire","","Nom.","dBA","53","53","54"]
["","Încălzire","","Nom.","dBA","57","57","57"]
["Agent frigorific","Tip","","","","R-32","R-32","R-32"]
["","Agent frigorific-=-Încărcare-=-kg","","","kg","","2.60"]
["Agent frigorific","GWP","","","","","675"]
["Agent frigorific","Cantitate","","","tCO2Eq","1.76","1.76","1.96"]
["Racorduri conducte","Lichid","","Dext","mm","9.52","9.52","9.52"]
["Piping connections","Gaz","","Dext","mm","","15.9"]
["Racorduri tubulatură","Lungime tubulatură","Max.","OU - IU","m","30","30","30"]
["","","Sistem","Echivalent","m","50","50","50"]
["Racorduri ţevi","Lungime tubulatură","Sistem","Fără încărcare","m","30","30","30"]
["","Încărcare suplimentară de agent frigorific","","","kg/m","A se vedea manualul de instalare","A se vedea manualul de instalare","A se vedea manualul de instalare"]
["","Diferenţa de nivel","IU - OU","Max.","m","30.0","30.0","30.0"]
["","","IU - IU","Max.","m","0.5","0.5","0.5"]
["Accesorii standard","Installation manual","","","","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1"]
["","General safety precautions","","","","1","1","1"]
["","LOT10 Energy Label","","","","1","1","1"]
["","Tie-wraps","","","","2","2","2"]
["Alimentare electrică","Fază","","","","3~","3~","3~"]
["Alimentare curent","Alimentare curent-=-Frecvenţă","","Frecvenţă","","50","50","50"]
["","Alimentare curent-=-Tensiune","","Tensiune","","380-415","380-415","380-415"]
["Curent - 50 Hz","Curent - 50 Hz-=-Curent maxim la siguranţe (MFA)","","Curent - 50 Hz-=-Curent maxim la siguranţe (MFA)-=-A","","","16"]
["Note","","","","","","(1) - Măsurat în conformitate cu ENER Lot 21","(1) - Măsurat în conformitate cu ENER Lot 21"]
["Greutate","Unitate","","","kg","70","","77"]
["Compresor","Tip","","","","Compresor swing etanşat ermetic","","Compresor swing etanşat ermetic"]
["Agent frigorific","Cantitate","","","kg","2.60","","2.90"]
["","GWP","","","","675","","675"]
["Racorduri conducte","Gaz","","Dext","mm","15.9","","15.9"]
["Curent - 50 Hz","Curent maxim la siguranțe (MFA)","","","A","16","","16"]