{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":43,"n_cols":13,"rows_kept":43,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAD-TZSSC2"]
[]
[]
[]
[]
["","","","","","EWADH13TZSSC2","EWADH17TZSSC2","EWADH12TZSSC2","EWADC16TZSSC2","EWADH18TZSSC2","EWADC15TZSSC2","EWADH11TZSSC2","EWADH19TZSSC2"]
["Capacitate de răcire","Nom.","","","kW","1,355","1,766","1,259","1,644","1,875","1,508","1,189","1,965"]
["Control capacitate","Metodă","","","","Variabilă","Variabilă","Variabilă","Variabilă","Variabilă","Variabilă","Variabilă","Variabilă"]
["","Capacitate minimă","","","%","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["Putere intrare","Răcire","","Nom.","kW","438.6","581.8","413.4","532.8","636.4","485","380.9","709.3"]
["EER","","","","","3.09","3.04","3.05","3.09","2.95","3.11","3.12","2.77"]
["IPLV","","","","","4.78","5.07","4.8","5.11","5.04","5.14","4.85","4.99"]
["SEER","","","","","4.65","4.86","4.64","4.87","4.83","4.83","4.69","4.68"]
["Dimensiuni","Unitate","","Adâncime","mm","11,404","13,202","10,510","12,302","14,102","11,404","10,510","14,102"]
["","","","Înălțime","mm","2,540","2,540","2,540","2,540","2,540","2,540","2,540","2,540"]
["","","","Lățime","mm","2,282","2,282","2,282","2,282","2,282","2,282","2,282","2,282"]
["Greutate","Greutate în timpul funcţionării","","","kg","11,123","12,575","9,879","12,145","13,048","11,727","9,879","13,048"]
["","Unitate","","","kg","10,112","11,564","9,322","11,134","12,037","10,716","9,322","12,037"]
["Carcasă","Culoare","","","","Alb fildeş","Alb fildeş","Alb fildeş","Alb fildeş","Alb fildeş","Alb fildeş","Alb fildeş","Alb fildeş"]
["","Material","","","","Tablă de oţel galvanizat şi vopsit","Tablă de oţel galvanizat şi vopsit","Tablă de oţel galvanizat şi vopsit","Tablă de oţel galvanizat şi vopsit","Tablă de oţel galvanizat şi vopsit","Tablă de oţel galvanizat şi vopsit","Tablă de oţel galvanizat şi vopsit","Tablă de oţel galvanizat şi vopsit"]
["Condensator răcit cu aer","Tip","","","","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal"]
["Ventilator","Cantitate","","","","24","28","22","26","30","24","22","30"]
["","Tip","","","","Elice directă","Elice directă","Elice directă","Elice directă","Elice directă","Elice directă","Elice directă","Elice directă"]
["Motor ventilator","Acționare","","","","Pornit/Oprit","Pornit/Oprit","Pornit/Oprit","Pornit/Oprit","Pornit/Oprit","Pornit/Oprit","Pornit/Oprit","Pornit/Oprit"]
["Compressor","Cantitate_","","","","2","2","2","2","2","2","2","2"]
["","Tip","","","","Compresor cu un singur şurub controlat prin inverter","Compresor cu un singur şurub controlat prin inverter","Compresor cu un singur şurub controlat prin inverter","Compresor cu un singur şurub controlat prin inverter","Compresor cu un singur şurub controlat prin inverter","Compresor cu un singur şurub controlat prin inverter","Compresor cu un singur şurub controlat prin inverter","Compresor cu un singur şurub controlat prin inverter"]
["","Starting method","","","","Acționat prin VFD","Acționat prin VFD","Acționat prin VFD","Acționat prin VFD","Acționat prin VFD","Acționat prin VFD","Acționat prin VFD","Acționat prin VFD"]
["Nivel de putere sonoră","Răcire","","Nom.","dBA","104","105","103","105","106","104","102","107"]
["Nivelul de presiune sonoră","Răcire","","Nom.","dBA","82","82","81","82","83","81","80","84"]
["Agent frigorific","Tip","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","GWP","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Charge","","","kg","200","250","175","220","270","200","175","270"]
["","Circuite","","Cantitate","","2","2","2","2","2","2","2","2"]
["Racorduri conducte","Intrare/ieşire apă evaporator (dext)","","","","273","273","219.1","273","273","273","219.1","273"]
["Power supply","Fază","","","","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frecvenţă","","","Hz","50","50","50","50","50","50","50","50"]
["","Tensiune","","","V","400","400","400","400","400","400","400","400"]
["","Variaţie admisă a tensiunii","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10","10","10"]
["Unitate","Curent de pornire","","Max.","A","0","0","0","0","0","0","0","0"]
["","Curent de funcţionare","Răcire","Nom.","A","733.0","962.8","691.1","884.0","1,044","813.9","646.5","1,149"]
["","","","Max.","A","1,027","1,301","969","1,205","1,398","1,165","913","1,487"]
["","Curent maxim pe aparat pentru calibrarea conductorilor","","","A","1,130","1,431","1,066","1,326","1,538","1,282","1,004","1,636"]