{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":69,"n_cols":8,"rows_kept":69,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXM-ATV3"]
[]
[]
[]
[]
["","","","","","FWXM10AATV3","FWXM15AATV3","FWXM20AATV3"]
["Capacitate de răcire","7/12 °C","","Min.","kW","0.75","1.15","1.32"]
["","","","Med.","kW","1.36","2.08","2.39"]
["","","","Max.","kW","2.12","2.81","3.30"]
["Capacitate de răcire sensibilă","7/12 °C","","Min.","kW","0.59","0.83","1.02"]
["","","","Med.","kW","1.04","1.51","1.84"]
["","","","Max.","kW","1.54","2.11","2.65"]
["Capacitate de încălzire","45/40 °C","","Min.","kW","0.82","1.20","1.47"]
["","","","Med.","kW","1.53","2.16","2.59"]
["","","","Max.","kW","2.21","3.02","3.81"]
["Putere absorbită","Min.","","","kW","0","0.01","0.01"]
["","Med.","","","kW","0.01","0.01","0.01"]
["","Max.","","","kW","0.02","0.02","0.03"]
["Viteză ventilator","Min.","","","rot/min","680.00","680.00","680.00"]
["","Med.","","","rot/min","1100.00","1100.00","1100.00"]
["","Max.","","","rot/min","1500.00","1500.00","1500.00"]
["Carcasă","Culoare","","","","încorporat","încorporat","încorporat"]
["","Material","","","","Fără carcasă","Fără carcasă","Fără carcasă"]
["Dimensiuni","Unitate","","Înălțime","mm","576","576","576"]
["","","","Lățime","mm","725","925","1125"]
["","","","Adâncime","mm","126","126","126"]
["","Unitate integrată","","Înălțime","mm","690","690","690"]
["","","","Lățime","mm","830","1030","1230"]
["","","","Adâncime","mm","210","210","210"]
["Greutate","Unitate","","","kg","12","15","18"]
["","Unitate ambalată","","","kg","13","16","19"]
["Ambalare","Material","","","","Carton","Carton","Carton"]
["","Greutate","","","kg","1","1","1"]
["Schimbător de căldură","Cantitate","","","","1","1","1"]
["","Volumul intern al serpentinei","","","l","0.8","1.13","1.46"]
["","Încărcare","","Presiune de funcţionare","bar","10","10","10"]
["Circuit de apă","Diametru racorduri ţevi","","","in","3/4","3/4","3/4"]
["","Material conducte","","","","CUPRU","CUPRU","CUPRU"]
["","Presiune","Încălzire","Max.","bar","10","10","10"]
["Circuit de apă - pierdere de presiune de apă","Încălzire","45/40 °C","Min.","kPa","1.50","2.70","3.00"]
["","","","Med.","kPa","4.30","9.30","8.90"]
["","","","Max.","kPa","9.20","19.10","21.20"]
["","Răcire","7/12 °C","Min.","kPa","1.90","2.70","2.50"]
["","","","Med.","kPa","4.30","9.90","8.80"]
["","","","Max.","kPa","8.20","17.10","18.00"]
["Circuit de apă - debit de apă","Încălzire","45/40 °C","Min.","kg/h","140.00","210.00","260.00"]
["","","","Med.","kg/h","270.00","380.00","450.00"]
["","","","Max.","kg/h","390.00","530.00","660.00"]
["","Răcire","7/12 °C","Min.","kg/h","130.00","200.00","230.00"]
["","","","Med.","kg/h","230.00","360.00","410.00"]
["","","","Max.","kg/h","360.00","480.00","570.00"]
["Nivel de putere sonoră","Min.","","","dBA","35","36","36"]
["","Med.","","","dBA","45","46","47"]
["","Max.","","","dBA","53.0","54.0","55.0"]
["Gama de operare","Încălzire","Partea de apă","Min.","°C","30","30","30"]
["","","","Max.","°C","85","85","85"]
["","Răcire","Partea de apă","Min.","°C","5","5","5"]
["","","","Max.","°C","18","18","18"]
["","Instalarea în interior","Ambiant","Min.","°CDB","0","0","0"]
["","","","Max.","°CDB","45","45","45"]
["Sisteme de control","Telecomandă cu infraroșii","","","","Nu","Nu","Nu"]
["","Integrat în unitatea interioară","","","","Da","Da","Da"]
["Alimentare electrică","Fază","","","","1~","1~","1~"]
["Alimentare curent","Frecvenţă","","","Hz","50","50","50"]
["","Tensiune","","","V","230","230","230"]
["Consum de curent electric","Max.","","","W","19","20","29"]
["","Mod aşteptare","","","W","3","4","5"]
["Curent","Curent maxim de funcţionare","","Încălzire","A","0.16","0.18","0.26"]
["","","","Răcire","A","0.16","0.18","0.26"]