{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":38,"n_cols":6,"rows_kept":38,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXM-A8"]
[]
[]
[]
[]
["","","","","","RXM50A5V1B8"]
["Dimensiuni","Unitate","","Înălțime","mm","610"]
["","","","Lățime","mm","923"]
["","","","Adâncime","mm","367"]
["Greutate","Unitate","","","kg","40"]
["Motor ventilator","Viteză","Răcire","Super scăzută","rot/min","600"]
["Compresor","Tip","","","","Compresor swing etanşat ermetic"]
["Gama de operare","Răcire","Ambiant","Min.","° C termometru uscat","-10"]
["","","","Max.","° C termometru uscat","50 (1), 46 (1)"]
["","Încălzire","Ambiant","Min.","°C termometru umed","-21 (1), -15 (1)"]
["","","","Max.","°C termometru umed","18"]
["Nivelul de presiune sonoră","Răcire","","Nom.","dBA","48"]
["","Încălzire","","Nom.","dBA","49"]
["Agent frigorific","Tip","","","","R-32"]
["","Cantitate","","","kg","0.95"]
["","Cantitate","","","tCO2Eq","0.65"]
["","GWP","","","","675"]
["Racorduri tubulatură","Lungime tubulatură","Max.","OU - IU","m","30"]
["Racorduri ţevi","Încărcare suplimentară de agent frigorific","","","kg/m","0,02 (pentru lungimi ale tubulaturii care depăşesc 10 m)"]
["","Diferenţa de nivel","IU - OU","Max.","m","20"]
["Accesorii standard","Installation manual","","","","1"]
["","Drain joint","","","","1"]
["","Refrigerant charge label","","","","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1"]
["","General safety precautions","","","","1"]
["","LOT10 Energy Label","","","","1"]
["","Drain cap","","","","3"]
["Alimentare electrică","Fază","","","","1~"]
["Alimentare curent","Frecvenţă","","","Hz","50"]
["","Tensiune","","","V","220-240"]
["Note","","","","","(1) - Vezi desenele separate pentru domeniul de funcţionare"]
["","","","","","(2) - Vezi desenele separate pentru datele electrice"]
["","","","","","(3) - Conţine gaze fluorurate cu efect de seră"]