{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":32,"n_cols":6,"rows_kept":32,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXTA-B"]
[]
[]
[]
[]
["","","","","","RXTA30B2V1B"]
["Dimensiuni","Unitate","","Înălțime","mm","551"]
["","","","Lățime","mm","763"]
["","","","Adâncime","mm","312"]
["Greutate","Unitate","","","kg","38"]
["Motor ventilator","Viteză","Răcire","Super scăzută","rot/min","450"]
["","","Încălzire","Super scăzută","rot/min","360"]
["Compresor","Tip","","","","Compresor swing etanşat ermetic"]
["Gama de operare","Răcire","Ambiant","Min.","°CDB","-10"]
["","","","Max.","°CDB","46"]
["","Încălzire","Ambiant","Min.","°C termometru umed","-25"]
["","","","Max.","°C termometru umed","18"]
["Nivelul de presiune sonoră","Răcire","","Nom.","dBA","48"]
["","Încălzire","","Nom.","dBA","49"]
["Agent frigorific","Tip","","","","R-32"]
["","Cantitate","","","kg","1.1"]
["","Cantitate","","","tCO2Eq","0.74"]
["","GWP","","","","675"]
["Racorduri tubulatură","Lungime tubulatură","Max.","OU - IU","m","20"]
["Racorduri ţevi","Încărcare suplimentară de agent frigorific","","","kg/m","0,02 (pentru lungimi ale tubulaturii care depăşesc 10 m)"]
["","Diferenţa de nivel","IU - OU","Max.","m","15"]
["Accesorii standard","Installation manual","","","","1"]
["","Refrigerant charge label","","","","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1"]
["Alimentare electrică","Fază","","","","1~"]
["Alimentare curent","Frecvenţă","","","Hz","50"]
["","Tensiune","","","V","220-240"]